| Waikato Building Consents |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Compliance Schedule Details: SS 16 – Cable Cars |  |  |  |  |  |  |  |  |  |
| Please provide the following information with your Building Consent Application and Code Compliance Certificate Application if applicable. (If you need help to complete this form, consult the system provider or an IQP who is registered for the system above) |  |  |  |  |  |  |  |  |  |
| Applicant Name: ……………………………………..……..… Site Address: ……………………………………….…………. ………………………………………………………………..…. Existing Compliance Schedule Number(s): (if applicable) ………………………………….............................................. ………………………………….............................................. |  |  |  |  |  |  | Building Name: …………………………………..…………… Installation provider: (if known) ……………………………… ………………………………….............................................. Risk / Purpose group: …………………………….………….. Fire Hazard Category: ……………………….………………. Total Occupant Load: ……………………….……………….. |  |  |
| SPECIFIED SYSTEM DESCRIPTION (address those items that apply) |  |  |  |  |  |  |  |  |  |
| Specified systems are: |  |  |  | £ Existing £ New £ Modified £ Removed |  |  |  |  |  |
| Type: |  | £ A cable car attached to or servicing a building used as a single household unit £ A ski chair lift which carries people in an enclosed vehicle and operates wholly or partially inside a building. £ Other: [specify] …………………………………………………………………………………………………… |  |  |  |  |  |  |  |
| Location Plan for exits and records is attached: £ YES £ NO |  |  |  |  |  |  |  |  |  |
| No. | Location |  |  |  |  | Make (Main components) |  |  | Model |
| 1 |  |  |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
|  | If needed continue the list on another sheet of paper |  |  |  |  |  |  |  |  |
| STANDARDS (address those items that apply) |  |  |  |  |  |  |  |  |  |
| Specifically, designed solutions do not apply if the system has been installed against a specific Standard / document. |  |  |  |  |  |  |  |  |  |
| Performance / installation: |  |  | £ NZS 5270:2005 Cable cars for private residences - Design, construction, installation and maintenance. (Original Version – 20 December 2005) £ Specifically, designed solution prepared by a person who, on the basis of experience and qualifications, is competent to do so. (Details provided) £ Other: ……………………………… |  |  |  |  |  |  |
| Inspections: |  |  | £ NZS 5270:2005 (Original Version – 20 December 2005) – Section 18 £ Other: ……………………………… |  |  |  |  | £ Specifically, designed solution prepared by a person who, on the basis of experience and qualifications, is competent to do so. (Details provided) |  |
| Maintenance: |  |  | £ NZS 5270:2005 (Original Version – 20 December 2005) – Section 16 and 17 £ Other: ………………………………. |  |  |  |  | £ Specifically, designed solution prepared by a person who, on the basis of experience and qualifications, is competent to do so. (Details provided) Continue on the next page |  |
| INSPECTIONS, MAINTENANCE AND REPORTING (address those items that apply) |  |  |  |  |  |  |  |  |  |
| Minimum inspection and maintenance procedures: |  |  |  |  | Regular inspections, testing and planned preventative maintenance and responsive maintenance will be done according to the nominated performance and inspection Standard/document, to ensure the system will always operate safely. |  |  |  |  |
| Inspection & Maintenance - frequency and responsibility: |  |  |  |  | Depending on the type of installation and its performance standard/document: £ Specifically, designed solutions: by IQP only. £ Standard /other document: NZS 5270: by IQP only |  |  |  |  |
| Inspections & Maintenance: Six-Monthly / Annual inspections. |  |  |  |  | Machinery Space - Visual inspection of machine supports, holding down bolts, etc. - Check condition of machinery enclosure and its access. - Check there are no obstructions or rubbish in or around the machinery enclosure. - Check that lighting in machinery are functions. - Check for presence of circuit diagrams and instruction manual. Machinery - Check condition of drum or traction sheave, with special attention to grooves - Check the condition and operation of the brake and condition of brake linings. - Check the running of machines, gearboxes, motors and their bearings. Runway - Inspect and test safety gear. - Visual check of runway - Check rope for attachments and terminations correct and in good condition, number of broken wires within acceptable limits, fillings not being shed, in generally good condition. - Visual check of guide rails for straightness and security. - Check there are no obstructions or rubbish along the track. - Check function of any lighting. - Check drainage at bottom of track. - Visual check of buffer condition. Car - Check functioning of any car lighting. - Check condition of guides or rollers. - Check function of car controls. - Observe operation of powered doors (if applicable). - Check load rating plate present. - Check correct operation of alarms and emergency telephone (if applicable). - Check any exit arrangement. Landing Doors - Check door interlocks. Operation - Check operation of door interlocks, limit switches, slack rope switch, stop switches and other safety switches. - Check operation of overload detector. Landings - Check stopping at landings. - Check landing controls. - Check condition of landing barriers. General - Visual check for any repairs or modifications done incorrectly. - Check maintenance records are properly kept. |  |  |  |  |
| Reporting: |  |  |  |  | The owner will keep records of all inspections, maintenance and repairs undertaken in the previous 24 months. These will be recorded in the On-Site Logbook, which will remain on the premises with the most recent compliance schedule, and as a minimum include: - Details of any inspection, test or preventative maintenance carried out, including dates, works undertaken, faults found, remedies applied and the person who performed the work. - Form 12A provided annually by the IQP. |  |  |  |  |